# Data-driven adaptive predictive control for an activated sludge process

Mashitah C. Razali 1, Norhaliza Abdul Wahab2*, Syahira Ibrahim3, Azavitra Zainal4, M.F. Rahmat5, Ramon Vilanova6

1,2*,3,4,5 Control & Mechatronics Engineering, School of Electrical Engineering,

Universiti Teknologi Malaysia, 81310 Skudai Johor Bahru, Malaysia

6Dept. de Telecomunicació i Enginyeria de Sistemes, Universitat Autònoma de Barcelona (UAB), Spain

| Article Info |  | ABSTRACT |
| --- | --- | --- |
| Article history: Received Jun x, 20xx Revised Nov x, 20xx Accepted Dec x, 20xx |  | Data-driven control requires no information of the mathematical model of the controlled process. This paper proposes the direct identification of controller parameters of activated sludge process. This class of data-driven control calculates the predictive controller parameters directly using subspace identification technique. By updating input-ouput data using receding window mechanism, the adaptive strategy can be achieved. The robustness test and stability analysis of direct adaptive model predictive control are discussed to realize the effectiveness of this adaptive control scheme. The applicability of the controller algorithm to adapt into varying kinetic parameters and operating conditions is evaluated. Simulation results show that by a proper and effective excitation of direct identification of controller parameters, the convergence and stability of the implicit predictive model can be achieved. |
| Keywords: Data driven control Subspace identification Direct adaptive |  |  |
|  |  | This is an open access article under the CC BY-SA license. |
| Corresponding Author: Norhaliza Abdul Wahab, Control & Mechatronics Engineering, School of Electrical Engineering, Universiti Teknologi Malaysia, 81310 Skudai Johor Bahru, Malaysia. Email: aliza@fke.utm.my |  |  |

- INTRODUCTION

In the biological activated sludge process (ASP), microbial contaminants are used in influent wastewater to degrade organic matters and nutrients [1-3]. Due to the system’s dynamic uncertainties and highly nonlinearities in the microorganism’s growth kinetic model, control of activated sludge process is a challenge. Conventional controllers are designed based on mathematical model of ASP which requires the designer to spend lot of building the model from the basic laws of biomass mass balance. The differential equations derived are then transformed into a standard transfer function or state space and the control laws are then applied [4-7]. However, the principal control problems of ASP as found in literature can be briefly illustrated by the variability of the kinetic parameter [8-9], time-varying influent conditions, nonlinearities [10], delays, lack of accurate sensors [11], and the limited availability of the online measurements [12]. Therefore, adaptive control principles are the preferred design option [13-15].

The main issue in the design of predictive controller for ASP was how to implement an accurate internal predictive model which best describes the behavior of the biochemical process involved. In [16] the internal predictive model of the plant implemented neural networks for controller design. However, this method suffers from the fact that it requires much attention on the training data collection resulting in many approximations in this stage of the design, and huge validation experiments have to be done to accurately identify the model and it’s usually fails to track the variability of the kinetic parameters. In [17] the authors have built the internal model for prediction based on linearized state space model of the bioprocess which is definitely undesirable in cases of variability in the effluents or any changes in operating conditions. Subspace Identification techniques developed in nineties offers an attractive and effective solution for the issue of prediction model and has been deployed successfully in design of predictive controllers for multiple-input multiple-output processes [18]. The employment of the robust computational tools such as QR-decomposition has recently opened a wide area of research to develop a single step implementation for predictive controllers where only input-output data are processed to directly calculate controller parameters or namely “Model-free” control methods [19]. The results of [19-22] are some of the successful reports for this class of novel algorithms. However, they have not introduced any closed-loop stability analysis for the sake of practical implementation of the proposed controller. Most adaptive predictive controllers reported so far are only applied to linear systems or indirectly implemented.  Therefore, the stability involved can be easily examined and proved for several cases of infinite prediction horizon or when the open loop system can be accessed and is stable. However, when the system is nonlinear or when finite horizons is applied, only few approaches have been published and were limited to indirect schemes [23-24]. In this paper, a data-driven predictive controller for activated sludge process is applied which is also consider stability of the proposed controller.

- ACTIVATED SLUDGE MODEL DEVELOPMENT

The biological process is modeled from component-balance considerations and the obtained model is most often a highly complex and high-order non-linear system given by the following set of nonlinear differential equations [25]:

dX(t)dt= μtXt-Dt1+rXt+rD(t)Xr(t)			        (1)

dS(t)dt= -μ(t)YXt-Dt1+rSt+D(t)Sin			        (2)

dC(t)dt= -K0μtYXt-Dt1+rCt+KLaCs-Ct+D(t)Cin	        (3)

dXr(t)dt= Dt1+rX(t)-D(t)(β+r)Xr(t)			        (4)

where X(t), St, Xr(t), Ct are the state variables representing the biomass, the substrate, the recycled biomass and dissolved oxygen concentrations, respectively. Meanwhile, D(t) is the dilution rate, and r and β represent the ratio of recycled flow to influent flow and ratio of waste flow to influent flow, Sin and Cin respectively, which corresponds to the substrate and dissolved oxygen concentrations in the influent stream. In addition, Y is the cell mass; K0 is a constant term, Cs is the maximum dissolved oxygen concentration and KLa represents the oxygen mass transfer coefficient.

KLa= αW,  α>0						        (5)

The kinetic model of the specific cell mass production rate μt is given as [24].

μt=μmax S(t)Ks+S(t) C(t)Kc+C(t)					        (6)

where μmax is the maximum specific growth rate, Ks is the so-called affinity constant, expressing the dependency of the degradation rate on the concentration of pollutant S, and Kc is the saturation constant. Notice that all the above equations are only used here in this work to generate input-output (I/O) data and they will not be used in any stage of the controller design. For simulations purpose, the process parameters, kinetic parameters, and initial conditions are adopted, as shown in Tables 1-3, respectively.

| Table 1. Process parameters ϒ; 0.65. r; 0.6. β; 0.2. α; 0.018 m-3. K0; 0.5. Cs; 10 mgl-1. Sin; 200 mgl-1. Cin; 0.5 mgl-1. | Table 2. Kinetic parameters ϒ; 0.65. r; 0.6. β; 0.2. α; 0.018 m-3. K0; 0.5. Cs; 10 mgl-1. Sin; 200 mgl-1. Cin; 0.5 mgl-1. | Table 3. Initial conditions X(0); 215 mgl-1. S(0); 35 mgl-1. C(0); 6 mgl-1. Xϒ(0); 400 mgl-1. Sin; 200 mgl-1. Cin; 0.5 mgl-1. |
| --- | --- | --- |

- SUBSPACE BASED PREDICTOR IDENTIFICATION

The most commonly used technique in system identification is used throughout this paper, given by equations (7) and (8):

xt+1=Axt+But+Ket						        (7)

yt=Cxt+Dut+et						        (8)

where, xt∈Rn, is the system states with order n, ut∈RNu, is the input vector with Nu number of inputs, yt∈RNy is the output vector with Ny number of outputs and, ek is a white noise disturbance (innovations) sequence with covariance Σe. The matrices A∈Rn×n, B∈Rn×Nu, C∈Rn×Ny, D∈RNu×Ny and K∈RNy×Ny are the state, input, output, feed-forward and kalman gain matrices of the system. The following equations (9) to (11) are defined as fundamental subspace I/O matrix equations. The subscripts p here denotes “past” and f denotes “future” matrices for its respective variables.

Yp=ΓiXp+HidUp+HisEp					        (9)

Yf=ΓiXf+HidUf+HisEf						        (10)

Xf=AiXp+ΔidUp+ΔisEp						        (11)

where the extended observability matrix Γi, the reversed extended controllability matrix for deterministic input Δid and for stochastic input Δis, matrices Hid and His are the lower triangular Toeplitz matrices for both deterministic and stochastic parts, respectively. Assuming that the open-loop I/O data uk and yk for k=0,1,…,N-1 are available for the identification, define the past input, Up and future input, Uf  data matrices for equations (9-11) as follows:

Up≜U0i-1≜u0u1⋯uN-2iu1u2⋯uN-2i+1…ui-1…ui⋱      ⋯       ⋯   uN-i     		                       (12)

Uf≜Ui2i-1≜uiui+1⋯uN-iui+1ui+2⋯uN-i+1…u2i-1…u2i⋱      ⋯       ⋯   uN-1     		                       (13)

where Up, Uf∈RNui×N-2i. The subscripts k1k2 indicates that the first column of the subspace matrix/vector starts from the time step k1 and ends by the time step k2. Similar notation can be written for past and future output matrices. In subspace identification literature, the following short-hand notation is commonly used:

Wp=YpUp							        (14)

Yf=LwWp+LuUf		 				        (15)

Equation (15) is the subspace predictor equation where the parameters to be obtained contain system model information without completely identifying the parametric model of the system such as the conventional transfer function or state space representation of the system. In addition, LwRiNy×iNy+Nu: is the subspace matrix that corresponds to the past inputs and outputs. LuRiNy×iNu: is the subspace matrix that corresponds to the future input data or the deterministic inputs, and Lu=Hid. The problem of obtaining the best linear predictor of the future outputs Yf, given the past inputs and outputs in the form of Wp and the future inputs Uf can be written as a Frobenius norm minimization

minLw,LuYf-LwLuWpUfF2					        (16)

The least square problem in equation (16) can be solved by the orthogonal projection and can be implemented by forming a QR-decomposition of the matrix WpTUfTYfTTas follows:

WpUfYf=R1100R21R220R31R32R33Q1Q2Q3					       (17)

Thus, we can estimate optimal prediction Yf as described in equation (17). Lw, and Lu can be used to formulate an estimation of future outputs as follows:

yk⋮yk+i-1=Lwuk-i⋮uk-1yk-i⋮yk-1+Luuk⋮uk-i-1				        (18)

Equation (18) is a streamlined subspace-based linear predictor equation which can be written as,

yf=Lwwp+Luuf                                                                                             (19)

- DIRECT ADAPTIVE MODEL PREDICTIVE CONTROL

In the direct adaptive model predictive control (DAMPC) or so-called data driven method, the controller parameters are estimated directly from the measurements. Therefore, the system model is implicitly included and no explicit model is formulated at any stage of the implementation. The adaptive mechanism implemented here adjusts the predictive controller parameters to the changes in the process dynamics in every sampling time. The measured input-output data is collected over a sliding window. It can be noted that the data window used to identify the controller parameters or state matrices can be expressed in terms of future inputs, uf=ui-1⋯u2i-2T and measurement (past) inputs up=u0⋯ui-1T and outputs yp=y0⋯yi-1T. Here, two prediction problems are given at current time instant i and i+1 as shown in Fig. (2). The first prediction problem (t=i) represents the case for obtaining the optimal prediction of i future outputs yf=yi⋯yi-2i-1T using the information given in the previously stated data window up, yp and uf. The second prediction problem shows that the time instant slides from t=i to t=i+1, this differs from the data window (up, yp and uf) which is now slides from left to right. At every time step, for the new available input-output data, the MPC parameters are updated online according to the updated predictor gain matrices and a new control action is computed.

The cost function performance criterion used can be written in matrix form as,

J=(yf-rf)T Q yf-rf+∆uHcT R ∆uHc				        (20)

where,

rf=INyINy⋮INyrt+1 , ∆uHc=∆ut+1∆ut+2⋮∆ut+Hc

By incorporating the integral action to the subspace predictive model, equation (21) is derived:

yf=ϜNyyt+FNyLw∆wp+FNyLuHc∆uHc				        (21)

where,

FNy=INy⋯0⋮⋱⋮INy⋯INy and LuHc=LuIHcNu0Nu×Hc

Then, we can rewrite equation (20) as:

J=12∆uHcTΩ∆uHc+∆uHcTΞ				  	        (22)

with,

Ω=FNyLuHc TQFNyLuHc+R

Ξ=FNyLuHc TQFNyLw∆wp+ϜNyyt-rt+1

In this case, the model predictive law for the unconstrained case of the problem of equation (22) is derived, which can be simply solved by:

δJδ∆uHc=Ω∆uHc+Ξ=0

∆uHc= -Ω-1Ξ

Rewriting as below:

∆ut+1=-K∆wp∆wp-Keyt-rt+1  	(23)

with,

K∆wp= INu0Nu×Hc-1Nu K∆wp,Hc

Ke=INu0Nu×Hc-1NuKe,Hc

where K∆wp,Hc and Ke,Hc defined as,

K∆wp,Hc=FNyLuHc TQFNyLuHc+R-1FNyLuHc TQFNyLw

Ke,Hc=FNyLuHc TQFNyLuHc+R-1FNyLuHc TQ ϜNy

# 5      SIMULATION AND RESULTS

The implemented control system is a two inputs two outputs system. The manipulated variables are dilution rate, D and air flow rate, W. The objective is to control the outputs of substrate and dissolved oxygen. The weighting matrices are chosen as Q=diag(1,10) and R=diag(104,10-4). Meanwhile, the Prediction Horizon, Hp and Control Horizon, Hc were 35, and 5 respectively. The simulation result for both manipulated and controlled variables are depicted in Figure 1. The squared error performance index was chosen to evaluate the performance of the closed-loop system and it was found to be 445.2.

Figure 1. Closed-loop response of substrate, dissolved oxygen, dilution rate and airflow rate

# 5.1 Stability analysis of subspace based DAMPC

In this section, the stability of the DAMPC is investigated. The design methodology is based on receding horizon control, which is also used in a standard model predictive control (MPC) system design. However, the main differentiating part between the DAMPC and a commonly used MPC is the starting point in the design. The starting point for the usual design of MPC is the availability of a dynamic model that describes the system to be controlled. With given sufficient accuracy of the model, long prediction horizon and control horizon, the closed-loop stability of MPC is obtained. In contrast, the starting point for the design of subspace-based DAMPC is the availability of excitation test data for the system to be controlled. Here, the question on the closed-loop stability of DAMPC is associated with the excitation test data for the system, as well as the prediction horizon and control horizon.

Several simulations of DAMPC showed that large prediction horizons may also resulted in larger errors of predictions since the actual system is nonlinear and the prediction based on subspace matrices is linear. Also, the longer the prediction horizon, of the DAMPC would approach as the classical MPC. The focus of the investigation on stability of the closed-loop system was on the quantity and quality of the excitation test data. Particularly, simulation studies are carried out to investigate the effect of both the window size of data length and prediction horizon length and the closed-loop performance criterion for various numerical values are shown. The best results obtained were n=400 and Hp=35 for both window size length and prediction horizon, respectively. The relationship of closed-loop stability to the predictor estimation algorithm is proposed. It can be seen, if the prediction converges to the true value, the overall closed-loop system will be equivalent to the standard MPC. From the convergence analysis of this algorithm, if a long enough prediction horizon for estimation is used, then the multi-step ahead estimated predictions will converge to the true multi-step ahead predictions. This can be proven by looking through the linear equation used to calculate the estimated output prediction presented again as:

yf=Lwwp+Luuf						        (24)

From Equation (24), we can write equivalently:

yf≜ yfp+ yff							        (25)

where:

yfp: The natural response, or the effect of the initial conditions is considered to be deterministic since it resulted from the multiplication by the past inputs and outputs wp.

yff: The forced response which is clearly resulted from the effect of the input over the prediction horizon which is in fact the impulse response coefficients due to the future input increments.

yfp=CCA⋮CAi-1xk⇒ykp= CAi-1xk-i+1≜Lwwp			         (26)

yff=D0⋯0CBD⋯0…CAi-2B…CAi-3B⋱      ⋯       ⋯Dukuk+1⋮uk+i-1

⇒ykf=Duk+n=1i-1CAn-1Buk-n≜Luuf	  (27)

Due to the nature of this algorithm, it will converge globally, which is an important property with respects to the typical adaptive algorithms found in the literature. Here we can conclude that if the future inputs remain bounded we can assure the convergence and the stability of the implicit predictive model which can only be proven by investigating the values of the impulse coefficients incorporated into prediction gain matrices over the prediction horizon. Therefore, by plotting Lu for every manipulated variable, the convergence of the predictive model to the true value over the prediction horizon can be illustrated. Figure 2 shows the values of Lu for both the future dilution rate manipulated variable and airflow rate manipulated variable is bounded over the prediction horizon. Therefore, it ensures the convergence of the estimated output prediction to the true value accordingly.

Figure 2. a) Prediction gain coefficients of future dilution rate	b) Prediction gain coefficients of the future airflow rate

# 5.2   Robustness tests for closed-loop DAMPC

In order to access the closed-loop performance of the applied algorithm, a rigorous simulation analysis under different operating conditions and kinetic process parameters were considered and discussed in this section. The constant influent rates are considered while taking into accounted the kinetic model variations and different operation points. Two different performance criterions were calculated for each output (C: Dissolved Oxygen Concentration, and S: Substrate Concentration) which is the Integral Square Error (ISE) and the Integral Absolute Error (IAE) for the purpose of assessment. In Table 4 listed the ISE and IAE of the ASP outputs under the applied DAMPC with two different cases of operating conditions:

Case 1: The operating condition in this case is Sin=200 mgl-1 and Cin=0.5 mgl-1 with XSCXrT=215556400T and the varied kinetic parameters for the nonlinear term, μmax, Ks, and Kc.

Case 2: The operating condition in this case is Sin=200 mgl-1 and Cin=0.5 mgl-1 with, XSCXrT=217.789641.23486.1146435.5791T and the same varied kinetic parameters for the nonlinear term are also considered, μmax, Ks, and Kc.

Table 4: Performance test numerical values

|  |  | ISE |  | IAE |  |
| --- | --- | --- | --- | --- | --- |
|  |  | S | C | S | C |
| CASE 1 | μmax = 0.15 | 132.7 | 1.133 | 107.9 | 16.74 |
|  | Ks = 100 mgl-1 |  |  |  |  |
|  | Kc = 2 mgl-1 |  |  |  |  |
|  | μmax = 0.21 | 680.1 | 18.64 | 332.8 | 59.93 |
|  | Ks = 100 mgl-1 |  |  |  |  |
|  | Kc = 3 mgl-1 |  |  |  |  |
|  | μmax = 0.21 | 111.8 | 1.439 | 113.4 | 18.87 |
|  | Ks = 150 mgl-1 |  |  |  |  |
|  | Kc = 2 mgl-1 |  |  |  |  |
| CASE 2 | μmax = 0.15 | 150.4 | 1.262 | 117.3 | 17.3 |
|  | Ks = 100 mgl-1 |  |  |  |  |
|  | Kc = 2 mgl-1 |  |  |  |  |
|  | μmax = 0.21 | 462.2 | 13.57 | 246.2 | 46.2 |
|  | Ks = 100 mgl-1 |  |  |  |  |
|  | Kc = 3 mgl-1 |  |  |  |  |
|  | μmax = 0.21 | 114.5 | 1.514 | 115.1 | 19.2 |
|  | Ks = 150 mgl-1 |  |  |  |  |
|  | Kc = 2 mgl-1 |  |  |  |  |

Results in Table 4 show the applicability of the controller algorithm to adapt both varied kinetic parameters and operating conditions. Therefore, system outputs will be regulated and the input reference trajectories will be tracked, irregardless of the conditions imposed on the real plant. Furthermore, no explicit model is formulated for the plant and any prior information about initial operating conditions are not needed, neither does the kinetic parameters.

# CONCLUSION

In this paper, the design of the adaptive data-driven predictive controller for biological ASP is presented. The integration between the robustness and efficiency of subspace based predictor estimation principal (where only geometrical tools are deployed without involving into nonlinear optimization); and the power of advanced unconstrained MPC design methodology (where MIMO systems can be controlled successfully) contributed to a robust-stable DAMPC for nonlinear ASP. From the control perspective, this work can be seen as an important investigation in the field ‘model-free’ control design since it has shown that the methodology can cope with the same issues of the ‘model-based’ control methods. This include the ease tuning of MPC parameters particularly for multivariable systems. Although, only unconstrained case is considered in this paper, we anticipate that the robustness of the constrained case is naturally achieved. In conclusion, the results obtained from the implementation of the presented control methodology on nonlinear ASP, was encouraging, and it is proposed that these algorithms show much promise for further development and analysis in terms of storage requirements, calculation time, and analytical stability proofs to gain wide acceptance in industrial scale applications.

ACKNOWLEDGEMENTS

The authors would like to thank the Ministry of Education (MOE) PRGS vote R.J130000.7851.4L702 and the Universiti Teknologi Malaysia UTMHIR vote 08G74 for their financial and facility support of this work.

REFERENCES

[1]	H.G. Han and J.F. Qiao, "Prediction of activated sludge bulking based on a self-organizing RBF neural network," Journal of Process Control, vol. 22, pp. 1103-1112, 2012.

[2]   S. Huang, L. Zhang, H. Guo, P. Chen, W. Xia, and C. Hu, “Modeling and Optimization of the Activated Sludge Process,” in 2019 Chinese Control Conference (CCC), 2019, pp. 6481–6486.

[3]     V. Benito, J. Etxebarria, F. Goni-de-cerio, Inigo Gonzalez, P. Brettes, and A. Urkiaga, “Better understanding of the activated sludge process combining fluorescence-based methods and flow cytometry: A case study,” J. Environ. Sci., vol. 90, pp. 51–58, 2020.

[4]   	Korving H., De Niet A., Koenders P. and Neef R., “Model Based Control at WWTP Westpoort”, in Risk and Decision Analysis in Maintenance Optimization and Flood Management, Delft University Press, 2009, pp. 113 - 122.

[5]  Francesco Smarra et.al., Achin Jain, Tulliode Rubeis, Dario Ambrosini, AlessandroD’Innocenzo and Rahul Mangharam, “Data-driven model predictive control using random forests for building energy optimization and climate control,” Applied Energy, vol 226, pp. 1252 - 1272, 2018.

[6]    C. M. Chew, M. K. Aroua, M. A. Hussain, and W. M. Z. W. Ismail, “Evaluation of ultrafiltration and conventional water treatment systems for sustainable development: An industrial scale case study,” J. Clean. Prod., vol. 112, pp. 3152–3163, 2016.

[7]    H. J. Van Waarde, J. Eising, H. L. T. Fellow, IEEE, and M. K. C. Member, “Data informativity : a new perspective on data-driven analysis and control,” IEEE Trans. Automat. Contr., pp. 1–16, 2020.

[8]	A. Barwal, “Influence of Mathematical – Kinetic Models for the Removal of Organics and Nutrients from Municipal Wastewater in Moving Bed Biofilm Reactor,” Int. J. Sci. Res. Multidiscip. Stud., vol. 5, no. 8, pp. 66–76, 2019.

[9]     T. T. Lee, F. Y. Wang, and R. B. Newell, “Advances in distributed parameter approach to the dynamics and control of activated sludge processes for wastewater treatment,” Water Res., vol. 40, pp. 853–869, 2006.

[10]	A. Iratni, N. Chang, Fellow, and IEEE, “Advances in Control Technologies for Wastewater Treatment Processes: Status, Challenges, and Perspectives,” IEEE/CAA J. Autom. Sin., vol. 6, no. 2, pp. 337–363, 2019.

[11]   D. Choi and H. Park, “A hybrid artificial neural network as a software sensor for optimal control of a wastewater treatment process,” Water Res., vol. 35, no. 16, pp. 3959–3967, 2001.

[12]	E. Petre, D. Selișteanu, C. Șulea-Iorgulescu, and S. Mehedințeanu, “Mathematical Modelling and Control for an Activated Sludge Process in a Wastewater Treatment Plant,” IEEE, 2019.

[13]    Wahab, N. A., R. Katebi, et al. "Data-driven adaptive model-based predictive control with application in wastewater systems." Control Theory & Applications, IET, vol. 5, no. 6, pp. 803-812, 2011.

[14]  	C. Vlad, M. Sbarciog, et al. “Indirect Control of Substrate Concentration for a Wastewater Treatment Process by Dissolved Oxygen Tracking” Journal of Control Engineering and Applied Informatics, CEAI, vol.14, no.1, pp. 37-47, 2012

[15]   	K J. Astrom and B. Wittenmark, “Adaptive control”, Addison-Wesley, 1995.

[16]   	Sergiu, C., S. Mihaela, et al. “Predictive Control of a Wastewater Treatment Process”. International Journal of Computers, Communications & Control, vol. II, no. 2, pp. 132-142, 2008.

[17] 	W. Favoreel and B. De Moor, “SPC: Subspace predictive control.” Technical Report 98-49, Departement Eleck-trotechniek - Katholieke Universiteit Leuven, 1998.

[18] 	Overschee, Van. P., B. De Moor, “Subspace Identification for Linear Systems: Theory-Implementation-Applications”. Kluwer Academic Publishers, 1996.

[19]   	Zhong-ShengHou and Zhuo Wang, "From Model-based Control to Data-driven Control: Survey, Classification and  Perspective,” Information Science, vol. 235, pp. 3-35, 2013.

[20]   	R. Kadali, B. Huang, and A. Rossiter. “A data driven approach to predictive controller design.” Control Engineering Practice, vol. 11, no. 3, pp. 261–278, 2003.

[21]	Xiaosuo Luo and Yongduan Song, “Adaptive Predictive Control: A Data-Driven Closed-Loop Subspace Identification Approach,” Abstract and Applied Analysis, vol. 2014, pp. 1-11, 2014.

[22]  Julian B, Johannes K, Matthias A. M, Frank A, “Data-Driven Model Predictive Control with Stability and Robustness Guarantees,” System, vol. 1, pp.1-15, 2019.

[23]   	Hale, E. T. and S. J. Qin, “Subspace model predictive control and a case study”. American Control Conference, 2002. Proceedings of the 2002.

[24]   Yunkai Lv, Sun and Ronghu Chi, " Data-driven adaptive iterative learning predictive control. " in Proceedings of the IEEE 6th Data Driven Control and Learning Systems, China, 2017.

[25] 	Nejjari, F., B. Dahhou, et al. "Non-linear multivariable adaptive control of an activated sludge wastewater treatment process." International Journal of Adaptive Control and Signal Processing, vol. 13, no. 5, pp. 347-365, 1999.

BIOGRAPHIES OF AUTHORS

|  | Mashitah Che Razali received Bachelor of Engineering (Electrical - Instrumentation and Control) in July 2011 and Master of Engineering (Electrical) in December 2014 at Universiti Teknologi Malaysia. Currently working towards her PhD degree in Electrical Engineering at the same university. Her current research interest is regarding to the system modelling, closed loop control and optimisation based on neural network. Presently, working with Department of Diploma Studies at Universiti Teknikal Malaysia, Melaka. |
| --- | --- |
|  | Ir. Dr Norhaliza Abdul Wahab is currently an Associate Professor at Universiti Teknologi Malaysia (UTM). She is currently the Director for Control and Mechatronic Engineering at the School of Electrical Engineering, UTM. She completed her PhD in Electrical Engineering majoring in Control in July 2009. She is actively involved in researching and teaching in the field of industrial process control. Her expertise is in modelling and control of industrial process plant. Recently she has worked primarily on different types of domestic and industrial water and wastewater treatment technology towards optimization and energy saving system. |
|  | Syahira Ibrahim received her B. Eng. Hons (Electric-Control and Instrumentation) and MSc. of Engineering (Electrical) from Universiti Teknologi Malaysia in 2011 and 2015 respectively. She is currently working toward her PhD in process control at School of Elecrical Engineering, Universiti Teknologi Malaysia. Her current research interests include modeling of near-infrared spectroscopy and optimization of membrane filtration system using hybrid response surface methodology-artificial intelligent. |
|  | Azavitra Zainal is a Lecturer in the Universiti Kuala Lumpur Malaysian Institute of Industrial Technology (UniKL MITEC). She was received her Master's degree from Wakayama University, Japan. Currently, she is pursuing her Ph.D. in Electrical Engineering at Universiti Teknologi Malaysia. |
|  | Mohd Fua’ad Rahmat received degree in Electrical Engineering at Universiti Teknologi Malaysia in 1989. He started his Master degree by taught course specialized in Control System Engineering and graduated in 1993 at The University of Sheffield, UK. Subsequently, he pursued his PhD degree in Electronic Instrumentation Engineering at the School of Engineering, SheffieldHallam University, UK and graduated in 1996. Currently, he is a Professor in the Department of Control and Mechatronics Engineering, Faculty of Electrical Engineering, Universiti TeknologiMalaysia Skudai Johor. His field of specialization include System Identification and Estimation, Signal Processing, Process Tomography for Industrial Process, Process Control Instrumentation, Sensors and Actuators, Hydraulic and Pneumatic System. |
|  | Ramon Vilanova was born in Lleida, Spain, in 1968. He received the master’s and Ph.D. degrees from the Universitat Autònoma de Barcelona (UAB), in 1991 and 1996, respectively. He is currently a Lecturer with the School of Engineering, UAB, where develops educational task teaching subjects of signals and systems, automatic control and technology of automated systems. He is the author of several book chapters and has more than 100 publications in international congresses/journals. His research interests include methods of tuning of PID regulators, systems with uncertainty, analysis of control systems with several degrees of freedom, application to environmental systems, and the development of methodologies for the design of machine-man interfaces. He is a member of the IFAC. |